## Slide 1
NRL
Air to Water
Heat Pump
Chillers and Heat Recovery

## Slide 2
NRL Heat Pump

## Slide 3
Section 1a:
NRL Heat Pump Features

## Slide 4
NRL Heat Pump
25 sizes range from 166,000 to 3,400,000 BTU/H (13 to 260 Tons)
Pump and buffer tank options available
Intelligent defrost
131°F hot water output
COP up to 3.03 W/W in heating mode
Minimum of 2 refrigerant circuits in a single unit
2-pipe configuration for seasonal changeover
2 independent refrigeration circuits
Optimized in heating mode
Optional desuperheater
Optional hydronic kits
Inteligent defrost

## Slide 5
Advantages
The Aermec Advantage: Self contained units
Competitor
Aermec
Notes: 6/25/2009
‹#›
6/25/2009
‹#›
6/25/2009
‹#›
6/25/2009
‹#›
4

## Slide 6
Hydronic Option
Evaporator
Water filter
Air vent valve
Flow switch
All NRL units will come standard with strainers, Inlet and outlet transducers and a flow switch
Evaporator
Strainer
Inlet and outlet transducers
Flow Switch

## Slide 7
P4 - Pump and high head pump and standby pump
Hydronic KIT:
00 – Without
01 – Tank and low head pump
02 – Tanks and low head pump and standby pump
03 – Tank and high head pump
04 – Tanks and high head pump and standby pump
P1 – Pump low head
P2 – Low head pump and standby pump
P3 – Pump high head
NRL Multiscroll with R410A
Hydraulic Options

## Slide 8
Hydraulic Options
NRL Multiscroll with R410A

## Slide 9
NRL Heat Pump
Operating Limits Cooling

## Slide 10
NRL Heat Pump
Operating Limits Heating

## Slide 11
NRL Redundancy
NRL Multiscroll with R410A

## Slide 12
Section 1b:
Defrost

## Slide 13
Defrosting Heat Pumps
Aermec declares all defrost penalties in our certifications as it is a requirement in Europe. Competitors in North America do not as there the air to water heat pumps sold here are actually only certified as chillers
This chart shows the penalty that is paid between the temperatures of 31˚F 38˚F or the defrost zone. As you can see there would be a fair difference in efficiencies of units that do not declare defrost

## Slide 14
NRL Heat Pumps Intelligent Defrost
The intelligence is to start the defrost cycle at the right time Not too early (loss of efficiency) nor too late
The defrost operation starts when there is a decrease in pressure on the evaporator side which is a clear indication of ice production on the coils
Pressure decrease
Defrost
Defrost

## Slide 15
NRL Heat Pumps Intelligent Defrost

## Slide 16
NRL Heat Pumps Intelligent Defrost
Aermec includes a derate for defrost in the selections
 | Heating capacity 113/104F
 | [btu/h]
Nominal - 44.6 F | 885,690.00
EN14511:2013 - 35F | 605,781.00
35F, no defrost | 750,335.00
Defrost penalty at 35F = 19.3%

## Slide 17
Section 1c:
Case Studies

## Slide 18
Case Studies
Apple Spaceship California
Two NRL0550°H°A°I704 Aermec heat pumps provide the hot water needed for the restaurants

## Slide 19
Case Studies
Head Quarters Surrey BC
4 NRL Heat Pump RCMP
Installed 2011
Notice the heat recovery piping

## Slide 20
NRL Chillers &
Heat Recovery

## Slide 21
Section 2a:
NRL Chillers & Heat Recovery Features

## Slide 22
NRL: Heat Recovery Chillers
Optional buffer tank and pumps
  Low head or high head
  Single pump or redundant pumps
  VFD or constant speed

## Slide 23
NRL: Heat Recovery Chillers
1
2
3
4
5
6
Circuit 1
Circuit 2

## Slide 24
NRL: Heat Recovery Chillers
NRL Multiscroll with R410A

## Slide 25
NRL: Heat Recovery Chillers
If the cooling load is dominant but there is also a heating load, why reject the heat outside?
Heat recovery options:
  Desuperheater
  Total heat recovery

## Slide 26
NRL: Heat Recovery Chillers
Desuperheater is in series with the condenser
Only part of the condensation is done in the desuperheter
The rest is done in the external coils
Fan speed modulation is mandatory to control the heat pressure
Hot water up to 149°F
Typically heat recovery with a desuperheater is limited to 40% of the cooling capacity (depends on the criteria)

## Slide 27
NRL: Heat Recovery Chillers

## Slide 28
NRL: Heat Recovery Chillers

## Slide 29
Total Heat Recovery

## Slide 30
NRL: Heat Recovery Chillers
Global efficiency of 22.84 with
LCWT = 44F, and LHWT = 113F
Global efficiency of 16.99
with LCWT = 44F, and LHWT = 131F

## Slide 31
NRL: Heat Recovery Chillers

## Slide 32
NRL: Heat Recovery Chillers
Recovery is activated when:
  The unit is in cooling operation
  There is a HW request
  Recovery flow switch contact is closed
  Minimum 3 minutes have passed since the CP started
  Minimum 5 minutes have passed since previous switch to recovery mode
Recovery is de-activated once the recovery set point is satisfied

## Slide 33
Section 2b:
Case Studies

## Slide 34
NRL Case Studies
Surrey Memorial Hospital
3 x NRL3600TA
Total Recovery Chillers

## Slide 35
NRL Case Studies
TACC Heat Recovery Chillers
Two NRL1800**TA*I800
TACC Total Acute Care Hospital

## Slide 36
NRL Case Studies
NRL3600TA 100 Maughan Road BC
240 tons of cooling and 240 tons of free heat
Used for reheat and drying the Marijuana

## Slide 37
NRL Case Studies
CFB Base Edmonton
NRL2800**TA*I8P2

## Slide 38
NRL Case Studies
Condominiums in Vancouver
4 x NRL1800HDA*I800

## Slide 39
Thank you!
Notes: make intro